## L2 estimate
| 4.1.1. Design indoor air quality conditions - general building level information | [7 empty] | Method 1 - perceived air quality | l / (s.m2) | Category I | 550 | ODA (P) 1 - clean (below limits) except for occasional dust | ODA (G) 1 - clean (below limits) | SUP 1 - n/a for office & residential buildings | EN 16890 classes | EN 779 classes
| Floor area (m2) | Method applied | Outdoor air quality (particulates) | Outdoor air quality (gaseous pollutants) | Supply air quality | Filter specification |  |  | Method 2 - substance limit(s) in air | l / (s per person) | Category II | 800 | ODA (P) 2 - high contamination (<50% above limits) | ODA (G) 2 - high contamination (<50% above limits) | SUP 2 - rooms for permanent occupation | ePM10: 5% | G1
[6 empty] | 1st | 2nd | 3rd | Method 3 - predefined airflow rates | l / s | Category III | 1350 | ODA (P) 3 - very high contamination (>50% above limits) | ODA (G) 3 - very high contamination (>50% above limits) | SUP 3 - rooms with temporary occupation | ePM10: 10% | G2
| 2500 | Method 3 - predefined airflow rates | ODA (P) 2 - high contamination (<50% above limits) | ODA (G) 1 - clean (below limits) | SUP 2 - rooms for permanent occupation | ePM10: 85% |  |  | Other (please specify in embedded comment) |  | Category IV |  |  |  | SUP 4 - rooms with short-term occupation | ePM10: 15% | G3
[15 empty] | SUP 5 - rooms without occupation | ePM10: 20% | G4
[16 empty] | ePM10: 25% | M5
4.1.1. Design indoor air quality conditions - specific information for defined building zones | [15 empty] | ePM10: 30% | M6
Building zone/room | Floor area (m2) | Method applied | Ventilation performance category | Ventilation rate | Units | Design occupation rate (person/m2) | Upper CO2 limit (ppm above outdoor air) | Control range of relative humidity (%) | [7 empty] | ePM10: 35% | F5
[16 empty] | ePM10: 40% | F6
[16 empty] | ePM10: 45% | F7
[16 empty] | ePM10: 50% | F8
[16 empty] | ePM10: 55% | F9
[16 empty] | ePM10: 60% | GF
ePM10: 65%
ePM10: 70%
ePM10: 75%
ePM10: 80%
ePM10: 85%
ePM10: 90%
ePM10: 95%
ePM2.5: 5%
ePM2.5: 10%
ePM2.5: 15%
| 4.1.2. Target indoor air pollutants - general building level information | [14 empty] | ePM2.5: 20%
| Floor area (m2) | Indoor radon risk assessed? | Estimated exposure (Bq/m3) | Mould risk assessed? | Conclusion about mould assessment | [10 empty] | ePM2.5: 25%
ePM2.5: 30%
ePM2.5: 35%
ePM2.5: 40%
4.1.2. Target indoor air pollutants - specific construction products and materials | [15 empty] | ePM2.5: 45%
Construction product/material | Product type or application | Total VOCs (μg/m³) | R value | Formaldehyde (μg/m³) | Certified by labelling scheme? If so, which one? |  | Other relevant information? (e.g. specific limits/results for other VOCs etc.) | [8 empty] | ePM2.5: 50%
Ceiling tiles | All | [14 empty] | ePM2.5: 55%
Paints and varnishes | walls and ceiling | [14 empty] | ePM2.5: 60%
| floors and stairs | [14 empty] | ePM2.5: 65%
| doors and windows | [14 empty] | ePM2.5: 70%
Floor coverings | textile coverings | [14 empty] | ePM2.5: 75%
| laminate and flexible coverings | [14 empty] | ePM2.5: 80%
| wooden coverings | [14 empty] | ePM2.5: 85%
| associated adhesives and sealants | [14 empty] | ePM2.5: 90%
Renovation products | internal insulation | [14 empty] | ePM2.5: 95%
| interior surface treatments (e.g. to resist damp) | [14 empty] | ePM1: 5%
Other (please specify) | Other (please specify) | [14 empty] | ePM1: 10%
ePM1: 15%
ePM1: 20%
ePM1: 25%
ePM1: 30%
ePM1: 35%
ePM1: 40%
ePM1: 45%
ePM1: 50%
ePM1: 55%
ePM1: 60%
ePM1: 65%
ePM1: 70%
ePM1: 75%
ePM1: 80%
ePM1: 85%
ePM1: 90%
ePM1: 95%
Note on C2: Enter the usable floor area of the building zone.
Note on D2: Choose one of the EN 16798-1 types of method or "other" from the dropdown menu. In the latter case, try to explain more about the method in an embedded comment or design documentation.
Note on E2: Compares estimated outdoor air concentrations of PM2.5 and PM10 to limits set by the WHO, the European Commission or regional/national authoroities.
Note on F2: Compares estimated outdoor air concentrations of NOx, SOx and ozone with limits set by the WHO, the European Commission or regional/national authoroities. May refer also to other pollutants like benzene.
Note on G2: Define the quality of air needed to be supplied by the ventilation system. A lower number means purer air.
Note on H2: The larger the higher the ODA and the lower the SUP categories, the more filter stages and/or the finer the filter(s) needed. Up to three can be specified here, using the new EN 16890 classes (and NOT the old EN 779 classes).
Note on B8: Insert a suitable name or description that clearly identifies the zone or room being ventilated.
Note on C8: Enter the usable floor area of the building zone.
Note on D8: Choose one of the EN 16798-1 types of method or "other" from the dropdown menu. In the latter case, try to explain more about the method in an embedded comment or design documentation.
Note on E8: Category I refers to the highest ventilation performance/rate while Category IV refers to the lowest.
Note on F8: Depends on the method used, EN 16798-1 performance category chosen, the emission category of the building and the occupant density - necessary to refer to the relevant table(s) from B6 to B14 in EN 16798-1.
Note on G8: Choose the relevant units according to how the ventilation capacity has been sized (e.g. per area or per occupant numbers).
Note on I8: Especially relevant when EN 16798-1 method 2 is used (column D) for calculating design ventilation rates and a per person ventilation rate is defined.
Note on J8: Not normally required except in building locations where outdoor air humidity might be very high.
Note on C25: Enter the floor area of the building zone (gross or usuable area?).

## L3 measure
Level 3 - 4.1.2 Target indoor air pollutants |  | Representative area tested |  |  | Representative area tested |  |  | Level 3 - 4.1.1 IAQ conditions
[8 empty] | Representative area tested and time/date of test | Floor area (m2) | Method applied | Ventilation performance category | Ventilation rate | Units | Occupation rate (person/m2) | CO2 (ppm above outdoor air concentration) | Control range of relative humidity (%)
Nature of IAQ parameter | IAQ parameter | Design stage | Post completion (prior to occupation) | During occupation | Design stage | Post completion (prior to occupation) | During occupation
Pollutants predominantly from outdoor sources | Radon (Bq/m3)
PM2.5 (µg/m3)
PM10 (µg/m3)
Ozone (µg/m3)
Benzene (µg/m3)
Air quality aspects (from outdoor & indoor sources) | Relative humidity (%)
CO2 (ppm indoors)
CO2 (ppm outdoors)
Pollutants predominantly from indoor sources | Total VOC (µg/m3) | n/a |  |  | n/a
| Total CMR VOCs (µg/m3) | n/a |  |  | n/a
| R-value | n/a |  |  | n/a
| Formaldehyde (µg/m3) | n/a |  |  | n/a
Note on D2: To enter a description of the area covered by the sampling/monitoring data and some basics about typical occupation patterns. Efforts for in-situ measurements should focus on those areas with the highest occupation densities (people/m2) and occupancy rates (hours/day). Sampling efforts should always include the worst-case scenarios (e.g. highest occupation times).
Note on G2: To enter a description of the area covered by the sampling/monitoring data and some basics about typical occupation patterns. Efforts for in-situ measurements should focus on those areas with the highest occupation densities (people/m2) and occupancy rates (hours/day). Sampling efforts should always include the worst-case scenarios (e.g. highest occupation times).
Note on L3: To enter a description of the area covered by the sampling/monitoring data and some basics about typical occupation patterns. Efforts for in-situ measurements should focus on those areas with the highest occupation densities (people/m2) and occupancy rates (hours/day). Sampling efforts should always include the worst-case scenarios (e.g. highest occupation times).
Note on M3: Enter the usable floor area of the building zone.
Note on N3: Choose one of the EN 16798-1 types of method or "other" from the dropdown menu. In the latter case, try to explain more about the method in an embedded comment or design documentation.
Note on O3: Category I refers to the highest ventilation performance/rate while Category IV refers to the lowest.
Note on P3: Depends on the method used, EN 16798-1 performance category chosen, the emission category of the building and the occupant density - necessary to refer to the relevant table(s) from B6 to B14 in EN 16798-1.
Note on Q3: Choose the relevant units according to how the ventilation capacity has been sized (e.g. per area or per occupant numbers).
Note on S3: Especially relevant when EN 16798-1 method 2 is used for calculating design ventilation rates and a per person ventilation rate is defined.. Outdoor CO2 normally ranges from 350 to 500ppm.
Note on T3: Not normally required except in building locations where outdoor air humidity might be very high.