## User version
Input data
PV module & Inverter | [5 empty] | PV system losses
Installation configuration | [6 empty] | Use default values (Y/N) | N | Insert estimated losses in User values (%)
| Orientation (°) (S is 0°S, E is -90°E) | 0 | [6 empty] | Defined losses cannot be lower than Minimum values
| Inclination (°) | 20 |  |  |  |  | Losses | Default values (%) | Minimum values (%) | Typical values (%) | Average values (%) | User values (%) | Applied values (%)
| CSER Correction factor | 1
[7 empty] | Module mismatch | 3 | 1.5 | 2 | 1.75 | 1.8 | 1.8
| User requested PV power (kW) | 2.5 |  |  |  |  | DC wiring | 3 | 1 | 2 | 1.5 | 3 | 3
[7 empty] | Diodes and connectors | 1 | 0.3 | 0.5 | 0.4 | 0.5 | 0.5
PV module | [6 empty] | Soiling | 25 | 2 | 5 | 3.5 | 6 | 6
| Datasheet information | [5 empty] | Shading | 10 | 0.1 | 5 | 2.5 | 4.5 | 4.5
| Pmax (W) | 320 |  |  |  |  | AC wiring | 2 | 0.7 | 1 | 0.85 | 0.7 | 0.7
| PV module area (m2) | 1.657 |  |  |  |  | Inverter temperature derating | 1.8 | 0.1 | 1 | 0.55 | 1.5 | 1.5
| Efficiency (%) | 19.312 |  |  |  |  | …
…
| EN 61853 "Photovoltaic (PV) module performance testing and energy rating" | [5 empty] | …
| Climates | CSER | Hp (kWh/m2.year) |  |  |  |  | 38.2561 |  |  |  |  | 16.1943
| Subtropical arid | 0.887 | 2295.452
| Temperate coastal | 0.992 | 972.934
| Temperate continental | 0.915 | 1266.003
Inverter
| Microinverter (Y/N) | N
| AC rated power (kW) | 2.5
EN 50530 "Overall efficiency of grid connected photovoltaic inverters"
| Euroefficiency (%) | 96
Calculation
PV system configuration
PV system configuration - PV array
| User requested PV power (kW) | 2.5
| Installed PV modules | 8
| Installed PV power (kW) | 2.56
| Installed PV Area (m2) | 13.256
PV system configuration - Inverter
| AC rated power (kW) | 2.5
| Size ratio PV array/Inverter | 1.024
PV system configuration - Losses (%)
Losses (%)
| Default installation |  | 38.2561
| User defined installation |  | 16.1943
PV system Performance Ratio calculation
Calculated Performance Ratio
PV module
|  | & | PV system losses
| Climates | Inverter | Default | User defined
| Subtropical arid | 0.85152 | 0.61744 | 0.83806
| Temperate coastal | 0.95232 | 0.61744 | 0.83806
| Temperate continental | 0.8784 | 0.61744 | 0.83806
PV system Performance Ratio
PV system configuration
| Climates | Default | User defined
| Subtropical arid | 0.52576 | 0.71362
| Temperate coastal | 0.588 | 0.7981
| Temperate continental | 0.54236 | 0.73615
PV system Energy Yield estimation
Input
| Reference climate (SA/TS/TN)* | SA |  | PV module (W) | 320
| PV system config (C1/C2)* | C2 |  | PV module (m2) | 1.657
| Installed PV array power (kW) | 2.56 |  | Hp (kWh/m2.yr) | 2295.452
| PV system Lifetime (yrs) | 30 |  | CSER corrected | 0.887
| PV system Degradation (%) | 1 |  | PV syst loss (%) | 16.1943
Results
Defined PV system |  |  | kWh | kWh/kWp | kWh/(kWp.m2)
| PV system AC Energy yield | Year 0 | 4193.5014 | 1638.0865 | 123.5732
|  | Lifetime | 106934.2857 | 41771.2054 | 3151.1169
Various possible locations and configurations
Lifetime PV system AC Energy yield (kWh/kWp.m2)
|  | PV system configuration |  | Energy Label
| Climates | Default | User defined | Default | User defined
| Subtropical arid | 2321.5855 | 3151.1169 | D | C
| Temperate coastal | 1100.4945 | 1493.715 | D | B
| Temperate continental | 1320.8353 | 1792.7862 | D | C
Nomenclature * |  | Energy Label based on Energy Yield intervals
Reference climates |  |  | Lifetime AC Energy yield (kWh/(kWp.m2))
SA | Subtropical arid | Energy Label | Subtrop arid | Temp coastal | Temp continental
TS | Temperate coastal | A | > 3857 | > 1682 | > 2173
TN | Temperate continental | B | [3857 - 3190) | [1682 - 1394) | [2173 - 1801)
|  | C | [3190 - 2524) | [1394 - 1106) | [1801 - 1429)
PV system configuration - PV system losses |  | D | [2524 - 1857) | [1106 - 818) | [1429 - 1057)
C1 | Default installation | E | [1857 - 1596) | [818 - 706) | [1057 - 912)
C2 | User defined installation | F | [1596 - 1334) | [706 - 594) | [912 - 767)
|  | G | ≤ 1334 | ≤ 594 | ≤ 767

## Azim_Tilt (hidden)
Subtropical arid | [7 empty] | CSER Subtropical arid
Pho - Spa: 38, -3.25 | [7 empty] | -999 | -180 | -150 | -120 | -90 | -60 | -30 | 0 | 30 | 60 | 90 | 120 | 150 | 180
[8 empty] | 0 | 0.885 | 0.885 | 0.885 | 0.885 | 0.885 | 0.885 | 0.885 | 0.885 | 0.885 | 0.885 | 0.885 | 0.885 | 0.885
Azimuth | Inclination | AOI | Spectral | TempIrrad |  |  |  | 5 | 0.881 | 0.882 | 0.884 | 0.886 | 0.887 | 0.888 | 0.887 | 0.887 | 0.886 | 0.884 | 0.883 | 0.881 | 0.881
0 | 20 | -2.7 | 0.4 | -8.7 |  |  |  | 10 | 0.876 | 0.879 | 0.883 | 0.887 | 0.889 | 0.889 | 0.889 | 0.888 | 0.886 | 0.883 | 0.88 | 0.877 | 0.876
|  | 3.5 | 0.3 | 8.6 | 11.5 | 11.5344 | 0.034397 | 15 | 0.87 | 0.875 | 0.882 | 0.888 | 0.89 | 0.891 | 0.89 | 0.888 | 0.886 | 0.882 | 0.877 | 0.871 | 0.87
|  | 2.6 | 0.4 | 8.8 | 10.8 | 10.8159 | 0.015885 | 20 | 0.863 | 0.87 | 0.881 | 0.888 | 0.891 | 0.892 | 0.891 | 0.889 | 0.886 | 0.882 | 0.874 | 0.865 | 0.863
|  | 2.7 | 0.4 | 8.8 | 10.8 | 10.9074 | 0.10745 | 25 | 0.857 | 0.865 | 0.88 | 0.888 | 0.892 | 0.893 | 0 | 0.889 | 0.886 | 0.88 | 0.871 | 0.859 | 0.857
|  | 6.7 |  | 9.2 | 15.2 | 15.2836 | 0.0836 | 30 | 0.854 | 0.86 | 0.878 | 0.889 | 0.893 | 0.893 | 0.892 | 0.89 | 0.885 | 0.879 | 0.869 | 0.853 | 0.854
[8 empty] | 35 | 0 | 0.857 | 0.877 | 0 | 0.893 | 0.894 | 0.893 | 0.889 | 0.885 | 0.878 | 0.866 | 0.848 | 0
[8 empty] | 40 | 0 | 0.853 | 0.876 | 0.889 | 0.893 | 0.895 | 0.893 | 0.889 | 0.884 | 0.877 | 0 | 0.843 | 0
[8 empty] | 45 | 0 | 0.849 | 0.875 | 0.888 | 0.894 | 0.896 | 0.894 | 0.89 | 0.884 | 0.876 | 0.862 | 0.838 | 0
[8 empty] | 50 | 0 | 0.845 | 0.874 | 0.888 | 0.894 | 0 | 0.895 | 0.891 | 0.885 | 0.875 | 0.86 | 0 | 0
[8 empty] | 55 | 0 | 0.841 | 0.873 | 0.888 | 0.894 | 0.897 | 0.896 | 0.891 | 0.884 | 0.874 | 0.857 | 0.828 | 0
[8 empty] | 60 | 0.784 | 0.838 | 0.871 | 0.887 | 0.896 | 0.898 | 0.897 | 0.891 | 0 | 0.873 | 0.855 | 0.823 | 0.784
[8 empty] | 65 | 0.766 | 0.834 | 0.87 | 0.888 | 0.896 | 0.899 | 0.897 | 0.891 | 0.883 | 0 | 0.852 | 0.818 | 0.766
[8 empty] | 70 | 0.755 | 0.829 | 0.867 | 0.887 | 0.895 | 0.899 | 0.896 | 0.891 | 0.883 | 0.871 | 0.849 | 0.813 | 0.755
[8 empty] | 75 | 0.754 | 0.823 | 0 | 0.885 | 0.896 | 0.899 | 0.895 | 0.89 | 0.881 | 0.868 | 0.845 | 0.806 | 0.754
[8 empty] | 80 | 0.747 | 0.816 | 0.861 | 0.886 | 0.896 | 0.898 | 0.893 | 0.888 | 0.88 | 0.865 | 0 | 0.799 | 0.747
[8 empty] | 85 | 0 | 0.808 | 0.857 | 0.883 | 0.895 | 0.896 | 0.889 | 0.885 | 0.879 | 0.865 | 0.836 | 0.789 | 0
[8 empty] | 90 | 0.723 | 0.798 | 0.852 | 0.88 | 0.894 | 0.892 | 0.883 | 0.88 | 0.875 | 0.86 | 0.83 | 0.78 | 0.723
GT
[8 empty] | -999 | -180 | -150 | -120 | -90 | -60 | -30 | 0 | 30 | 60 | 90 | 120 | 150 | 180
[8 empty] | 0 | 1640 | 1640 | 1640 | 1640 | 1640 | 1640 | 1640 | 1640 | 1640 | 1640 | 1640 | 1640 | 1640
[8 empty] | 5 | 1560 | 1580 | 1610 | 1640 | 1680 | 1700 | 1710 | 1700 | 1670 | 1630 | 1600 | 1570 | 1560
[8 empty] | 10 | 1470 | 1500 | 1560 | 1640 | 1710 | 1760 | 1770 | 1740 | 1690 | 1620 | 1540 | 1490 | 1470
[8 empty] | 15 | 1380 | 1420 | 1510 | 1630 | 1730 | 1800 | 1820 | 1780 | 1700 | 1600 | 1490 | 1400 | 1380
[8 empty] | 20 | 1270 | 1330 | 1460 | 1620 | 1750 | 1830 | 1850 | 1810 | 1710 | 1570 | 1430 | 1310 | 1270
[8 empty] | 25 | 1170 | 1240 | 1410 | 1590 | 1750 | 1850 | 0 | 1820 | 1710 | 1550 | 1370 | 1220 | 1170
[8 empty] | 30 | 1080 | 1160 | 1350 | 1570 | 1750 | 1860 | 1890 | 1830 | 1700 | 1520 | 1310 | 1130 | 1080
[8 empty] | 35 | 0 | 1070 | 1300 | 0 | 1740 | 1860 | 1890 | 1830 | 1690 | 1480 | 1250 | 1040 | 0
[8 empty] | 40 | 0 | 988 | 1240 | 1510 | 1720 | 1850 | 1890 | 1820 | 1660 | 1450 | 0 | 957 | 0
[8 empty] | 45 | 0 | 909 | 1180 | 1470 | 1700 | 1840 | 1860 | 1790 | 1630 | 1400 | 1130 | 876 | 0
[8 empty] | 50 | 0 | 831 | 1130 | 1430 | 1670 | 0 | 1830 | 1760 | 1600 | 1360 | 1070 | 0 | 0
[8 empty] | 55 | 0 | 758 | 1070 | 1380 | 1620 | 1770 | 1790 | 1720 | 1550 | 1310 | 1010 | 725 | 0
[8 empty] | 60 | 542 | 690 | 1010 | 1330 | 1570 | 1710 | 1740 | 1670 | 0 | 1250 | 952 | 657 | 542
[8 empty] | 65 | 464 | 626 | 951 | 1270 | 1520 | 1650 | 1670 | 1600 | 1440 | 0 | 893 | 595 | 464
[8 empty] | 70 | 397 | 568 | 892 | 1210 | 1450 | 1580 | 1600 | 1530 | 1380 | 1140 | 834 | 538 | 397
[8 empty] | 75 | 341 | 514 | 0 | 1150 | 1380 | 1500 | 1510 | 1450 | 1310 | 1070 | 776 | 486 | 341
[8 empty] | 80 | 295 | 463 | 771 | 1080 | 1300 | 1410 | 1410 | 1360 | 1230 | 1010 | 0 | 439 | 295
[8 empty] | 85 | 0 | 418 | 711 | 1010 | 1220 | 1310 | 1300 | 1260 | 1140 | 935 | 659 | 394 | 0
[8 empty] | 90 | 231 | 374 | 651 | 937 | 1130 | 1210 | 1190 | 1160 | 1060 | 861 | 601 | 353 | 231
Total losses
[8 empty] | -999 | -180 | -150 | -120 | -90 | -60 | -30 | 0 | 30 | 60 | 90 | 120 | 150 | 180
[8 empty] | 0 | -11.5 | -11.5 | -11.5 | -11.5 | -11.5 | -11.5 | -11.5 | -11.5 | -11.5 | -11.5 | -11.5 | -11.5 | -11.5 | -11.4
[8 empty] | 5 | -11.9 | -11.8 | -11.6 | -11.4 | -11.3 | -11.2 | -11.3 | -11.3 | -11.4 | -11.6 | -11.7 | -11.9 | -11.9
[8 empty] | 10 | -12.4 | -12.1 | -11.7 | -11.3 | -11.1 | -11.1 | -11.1 | -11.2 | -11.4 | -11.7 | -12 | -12.3 | -12.4
[8 empty] | 15 | -13 | -12.5 | -11.8 | -11.2 | -11 | -10.9 | -11 | -11.2 | -11.4 | -11.8 | -12.3 | -12.9 | -13
[8 empty] | 20 | -13.7 | -13 | -11.9 | -11.2 | -10.9 | -10.8 | -10.9 | -11.1 | -11.4 | -11.8 | -12.6 | -13.5 | -13.7
[8 empty] | 25 | -14.3 | -13.5 | -12 | -11.2 | -10.8 | -10.7 | -100 | -11.1 | -11.4 | -12 | -12.9 | -14.1 | -14.3
[8 empty] | 30 | -14.6 | -14 | -12.2 | -11.1 | -10.7 | -10.7 | -10.8 | -11 | -11.5 | -12.1 | -13.1 | -14.7 | -14.6
[8 empty] | 35 | -100 | -14.3 | -12.3 | -100 | -10.7 | -10.6 | -10.7 | -11.1 | -11.5 | -12.2 | -13.4 | -15.2 | -100
[8 empty] | 40 | -100 | -14.7 | -12.4 | -11.1 | -10.7 | -10.5 | -10.7 | -11.1 | -11.6 | -12.3 | -100 | -15.7 | -100
[8 empty] | 45 | -100 | -15.1 | -12.5 | -11.2 | -10.6 | -10.4 | -10.6 | -11 | -11.6 | -12.4 | -13.8 | -16.2 | -100
[8 empty] | 50 | -100 | -15.5 | -12.6 | -11.2 | -10.6 | -100 | -10.5 | -10.9 | -11.5 | -12.5 | -14 | -100 | -100
[8 empty] | 55 | -100 | -15.9 | -12.7 | -11.2 | -10.6 | -10.3 | -10.4 | -10.9 | -11.6 | -12.6 | -14.3 | -17.2 | -100
[8 empty] | 60 | -21.6 | -16.2 | -12.9 | -11.3 | -10.4 | -10.2 | -10.3 | -10.9 | -100 | -12.7 | -14.5 | -17.7 | -21.6
[8 empty] | 65 | -23.4 | -16.6 | -13 | -11.2 | -10.4 | -10.1 | -10.3 | -10.9 | -11.7 | -100 | -14.8 | -18.2 | -23.4
[8 empty] | 70 | -24.5 | -17.1 | -13.3 | -11.3 | -10.5 | -10.1 | -10.4 | -10.9 | -11.7 | -12.9 | -15.1 | -18.7 | -24.5
[8 empty] | 75 | -24.6 | -17.7 | -100 | -11.5 | -10.4 | -10.1 | -10.5 | -11 | -11.9 | -13.2 | -15.5 | -19.4 | -24.6
[8 empty] | 80 | -25.3 | -18.4 | -13.9 | -11.4 | -10.4 | -10.2 | -10.7 | -11.2 | -12 | -13.5 | -100 | -20.1 | -25.3
[8 empty] | 85 | -100 | -19.2 | -14.3 | -11.7 | -10.5 | -10.4 | -11.1 | -11.5 | -12.1 | -13.5 | -16.4 | -21.1 | -100
[8 empty] | 90 | -27.7 | -20.2 | -14.8 | -12 | -10.6 | -10.8 | -11.7 | -12 | -12.5 | -14 | -17 | -22 | -27.7

## Sheet3 (hidden)
Reference climates
SA | Subtropical arid
TS | Temperate coastal
TN | Temperate continental
PV system configuration
A | Default installation
B | Optimised design and yield forecasting
C | Optimised monitoring and maintenance
D | Poor Quality installation
PV system configuration - PV system losses
C1 | Default installation
C2 | User defined installation

## CSER norm (hidden)
Subtropical arid | [14 empty] | User | lower azim | upper azim | Subtropical arid
-999 | -180 | -150 | -120 | -90 | -60 | -30 | 0 | 30 | 60 | 90 | 120 | 150 | 180 | Azim | 0 | 0 | 0 | Point 1 | lower azim | upper azim | Point 2
0 | 0.99327 | 0.99327 | 0.99327 | 0.99327 | 0.99327 | 0.99327 | 0.99327 | 0.99327 | 0.99327 | 0.99327 | 0.99327 | 0.99327 | 0.99327 |  |  |  |  | lower incl | 1 | 1 | lower incl | Pont A | 1
5 | 0.98878 | 0.9899 | 0.99214 | 0.99439 | 0.99551 | 0.99663 | 0.99551 | 0.99551 | 0.99439 | 0.99214 | 0.99102 | 0.98878 | 0.98878 |  | User | lower incl | upper incl | upper incl | 1 | 1 | upper incl | Point B | 1
10 | 0.98316 | 0.98653 | 0.99102 | 0.99551 | 0.99776 | 0.99776 | 0.99776 | 0.99663 | 0.99439 | 0.99102 | 0.98765 | 0.98429 | 0.98316 | Incl | 20 | 20 | 20 | Point 3 | lower azim | upper azim | Point 4
15 | 0.97643 | 0.98204 | 0.9899 | 0.99663 | 0.99888 | 1 | 0.99888 | 0.99663 | 0.99439 | 0.9899 | 0.98429 | 0.97755 | 0.97643 | [8 empty] | Users | 1
20 | 0.96857 | 0.97643 | 0.98878 | 0.99663 | 1 | 1.0011 | 1 | 0.99776 | 0.99439 | 0.9899 | 0.98092 | 0.97082 | 0.96857
25 | 0.96184 | 0.97082 | 0.98765 | 0.99663 | 1.0011 | 1.0022 | 1.0011 | 0.99776 | 0.99439 | 0.98765 | 0.97755 | 0.96409 | 0.96184 | Ref clim | SA
30 | 0.95847 | 0.96521 | 0.98541 | 0.99776 | 1.0022 | 1.0022 | 1.0011 | 0.99888 | 0.99327 | 0.98653 | 0.97531 | 0.95735 | 0.95847 | norm factor | 1 |  |  | I haven't touched the last two climates yet
35 | 0.95174 | 0.96184 | 0.98429 | 0.99663 | 1.0022 | 1.0034 | 1.0022 | 0.99776 | 0.99327 | 0.98541 | 0.97194 | 0.95174 | 0.95174
40 | 0.94276 | 0.95735 | 0.98316 | 0.99776 | 1.0022 | 1.0045 | 1.0022 | 0.99776 | 0.99214 | 0.98429 | 0.9697 | 0.94613 | 0.94276 |  |  |  |  | Temperate continental
45 | 0.93154 | 0.95286 | 0.98204 | 0.99663 | 1.0034 | 1.0056 | 1.0034 | 0.99888 | 0.99214 | 0.98316 | 0.96745 | 0.94052 | 0.93154 |  |  |  |  | Point 1 | lower azim | upper azim | Point 2
50 | 0.91695 | 0.94837 | 0.98092 | 0.99663 | 1.0034 | 1.0067 | 1.0045 | 1 | 0.99327 | 0.98204 | 0.96521 | 0.93378 | 0.91695 |  |  |  |  | lower incl | 1 | 1 | lower incl | Pont A | 1
55 | 0.90011 | 0.94388 | 0.9798 | 0.99663 | 1.0034 | 1.0067 | 1.0056 | 1 | 0.99214 | 0.98092 | 0.96184 | 0.92929 | 0.90011 |  |  |  |  | upper incl | 1 | 1 | upper incl | Point B | 1
60 | 0.87991 | 0.94052 | 0.97755 | 0.99551 | 1.0056 | 1.0079 | 1.0067 | 1 | 0.9899 | 0.9798 | 0.9596 | 0.92368 | 0.87991 |  |  |  |  | Point 3 | lower azim | upper azim | Point 4
65 | 0.85971 | 0.93603 | 0.97643 | 0.99663 | 1.0056 | 1.009 | 1.0067 | 1 | 0.99102 | 0.97755 | 0.95623 | 0.91807 | 0.85971 | [8 empty] | Users | 1
70 | 0.84736 | 0.93042 | 0.97306 | 0.99551 | 1.0045 | 1.009 | 1.0056 | 1 | 0.99102 | 0.97755 | 0.95286 | 0.91246 | 0.84736
75 | 0.84624 | 0.92368 | 0.97082 | 0.99327 | 1.0056 | 1.009 | 1.0045 | 0.99888 | 0.98878 | 0.97419 | 0.94837 | 0.9046 | 0.84624
80 | 0.83838 | 0.91582 | 0.96633 | 0.99439 | 1.0056 | 1.0079 | 1.0022 | 0.99663 | 0.98765 | 0.97082 | 0.94388 | 0.89675 | 0.83838
85 | 0.82716 | 0.90685 | 0.96184 | 0.99102 | 1.0045 | 1.0056 | 0.99776 | 0.99327 | 0.98653 | 0.97082 | 0.93827 | 0.88552 | 0.82716
90 | 0.81145 | 0.89562 | 0.95623 | 0.98765 | 1.0034 | 1.0011 | 0.99102 | 0.98765 | 0.98204 | 0.96521 | 0.93154 | 0.87542 | 0.81145 |  |  |  |  | Temperate coastal
[18 empty] | Point 1 | lower azim | upper azim | Point 2
Temperate continental | [17 empty] | lower incl | 1 | 1 | lower incl | Pont A | 1
-999 | -180 | -150 | -120 | -90 | -60 | -30 | 0 | 30 | 60 | 90 | 120 | 150 | 180 |  |  |  |  | upper incl | 1 | 1 | upper incl | Point B | 1
0 | 0.99023 | 0.99023 | 0.99023 | 0.99023 | 0.99023 | 0.99023 | 0.99023 | 0.99023 | 0.99023 | 0.99023 | 0.99023 | 0.99023 | 0.99023 |  |  |  |  | Point 3 | lower azim | upper azim | Point 4
5 | 0.9848 | 0.98588 | 0.98806 | 0.99023 | 0.9924 | 0.99349 | 0.99349 | 0.9924 | 0.99131 | 0.98914 | 0.98697 | 0.9848 | 0.9848 | [8 empty] | Users | 1
10 | 0.97828 | 0.98154 | 0.98697 | 0.99131 | 0.99457 | 0.99674 | 0.99674 | 0.99457 | 0.9924 | 0.98806 | 0.98371 | 0.97937 | 0.97828
15 | 0.97177 | 0.97611 | 0.9848 | 0.9924 | 0.99674 | 0.99891 | 0.99891 | 0.99674 | 0.9924 | 0.98697 | 0.98046 | 0.97286 | 0.97177
20 | 0.96634 | 0.97177 | 0.98263 | 0.9924 | 0.99783 | 1 | 1 | 0.99783 | 0.99349 | 0.98588 | 0.97611 | 0.96743 | 0.96634
25 | 0.95874 | 0.96634 | 0.98154 | 0.99349 | 0.99891 | 1.0011 | 1.0011 | 0.99891 | 0.99349 | 0.98588 | 0.97394 | 0.96091 | 0.95874
30 | 0.95005 | 0.96091 | 0.98046 | 0.99349 | 1 | 1.0022 | 1.0022 | 0.99891 | 0.99349 | 0.9848 | 0.97068 | 0.9544 | 0.95005
35 | 0.94028 | 0.95548 | 0.97937 | 0.99349 | 1.0011 | 1.0043 | 1.0033 | 1 | 0.99349 | 0.98371 | 0.96851 | 0.94788 | 0.94028 |  |  |  |  | Values used to define the Energy Label
40 | 0.92834 | 0.95005 | 0.97828 | 0.99349 | 1.0022 | 1.0054 | 1.0043 | 1.0011 | 0.99349 | 0.98371 | 0.96743 | 0.94137 | 0.92834 |  |  |  |  | lower lim | Sub arid | T coastal | T cont
45 | 0.91531 | 0.94463 | 0.9772 | 0.99349 | 1.0022 | 1.0054 | 1.0054 | 1.0011 | 0.99349 | 0.98263 | 0.96526 | 0.93594 | 0.91531 | [5 empty] | 1000000 | 1000000 | 1000000
50 | 0.90228 | 0.94137 | 0.97503 | 0.99349 | 1.0022 | 1.0054 | 1.0065 | 1.0011 | 0.9924 | 0.98154 | 0.96308 | 0.93268 | 0.90228 |  |  |  |  | a | 3856.692 | 1682.2306 | 2172.9105
55 | 0.89142 | 0.93811 | 0.97394 | 0.9924 | 1.0033 | 1.0065 | 1.0065 | 1.0011 | 0.9924 | 0.97937 | 0.95983 | 0.92942 | 0.89142 |  |  |  |  | b | 3190.128 | 1394.1537 | 1800.9403
60 | 0.88491 | 0.93485 | 0.97068 | 0.9924 | 1.0033 | 1.0076 | 1.0065 | 1.0011 | 0.9924 | 0.97828 | 0.95657 | 0.92508 | 0.88491 |  |  |  |  | c | 2523.564 | 1106.0769 | 1428.9702
65 | 0.88491 | 0.92942 | 0.96743 | 0.99023 | 1.0022 | 1.0076 | 1.0065 | 1.0011 | 0.99023 | 0.97611 | 0.95331 | 0.91965 | 0.88491 |  |  |  |  | d | 1857 | 818 | 1057
70 | 0.87948 | 0.92291 | 0.96308 | 0.98914 | 1.0022 | 1.0065 | 1.0054 | 1 | 0.98806 | 0.97286 | 0.94897 | 0.91205 | 0.87948 |  |  |  |  | e | 1595.6211 | 706.1332 | 912.0919
75 | 0.87079 | 0.91531 | 0.95874 | 0.98588 | 1.0011 | 1.0054 | 1.0043 | 0.99783 | 0.98806 | 0.97068 | 0.94354 | 0.90337 | 0.87079 |  |  |  |  | f | 1334.2422 | 594.2665 | 767.1838
80 | 0.85993 | 0.90445 | 0.95223 | 0.98263 | 0.99891 | 1.0043 | 1.0022 | 0.99566 | 0.98588 | 0.96634 | 0.93702 | 0.89359 | 0.85993 |  |  |  |  | g
85 | 0.84582 | 0.89468 | 0.94571 | 0.97937 | 0.99566 | 1.0011 | 0.99891 | 0.9924 | 0.98154 | 0.96091 | 0.92942 | 0.88274 | 0.84582
90 | 0.8317 | 0.88165 | 0.93811 | 0.97503 | 0.99349 | 0.99674 | 0.9924 | 0.98697 | 0.9772 | 0.95657 | 0.92074 | 0.86971 | 0.8317
Temperate coastal
-999 | -180 | -150 | -120 | -90 | -60 | -30 | 0 | 30 | 60 | 90 | 120 | 150 | 180
0 | 0.9831 | 0.9831 | 0.9831 | 0.9831 | 0.9831 | 0.9831 | 0.9831 | 0.9831 | 0.9831 | 0.9831 | 0.9831 | 0.9831 | 0.9831
5 | 0.97782 | 0.97888 | 0.98099 | 0.98416 | 0.98733 | 0.98838 | 0.98838 | 0.98733 | 0.98627 | 0.9831 | 0.97994 | 0.97782 | 0.97782
10 | 0.97149 | 0.9736 | 0.97994 | 0.98522 | 0.9905 | 0.99261 | 0.99366 | 0.99155 | 0.98838 | 0.98416 | 0.97782 | 0.9736 | 0.97149
15 | 0.96621 | 0.96938 | 0.97782 | 0.98733 | 0.99366 | 0.99683 | 0.99683 | 0.99472 | 0.99155 | 0.98416 | 0.97571 | 0.96832 | 0.96621
20 | 0.95987 | 0.96515 | 0.97677 | 0.98838 | 0.99578 | 0.99894 | 1 | 0.99789 | 0.99261 | 0.98522 | 0.97466 | 0.9641 | 0.95987
25 | 0.95354 | 0.96093 | 0.97677 | 0.98944 | 0.99789 | 1.0021 | 1.0021 | 1 | 0.99472 | 0.98627 | 0.9736 | 0.95882 | 0.95354
30 | 0.94615 | 0.95671 | 0.97677 | 0.9905 | 1 | 1.0032 | 1.0042 | 1.0011 | 0.99578 | 0.98733 | 0.9736 | 0.95459 | 0.94615
35 | 0.93875 | 0.95248 | 0.97571 | 0.99155 | 1.0011 | 1.0053 | 1.0053 | 1.0032 | 0.99683 | 0.98733 | 0.97254 | 0.95037 | 0.93875
40 | 0.93031 | 0.94931 | 0.97571 | 0.99155 | 1.0011 | 1.0053 | 1.0063 | 1.0032 | 0.99789 | 0.98733 | 0.97149 | 0.9472 | 0.93031
45 | 0.92397 | 0.94826 | 0.97466 | 0.99155 | 1.0021 | 1.0063 | 1.0074 | 1.0042 | 0.99789 | 0.98627 | 0.97043 | 0.94509 | 0.92397
50 | 0.91763 | 0.94615 | 0.97254 | 0.9905 | 1.0021 | 1.0074 | 1.0074 | 1.0042 | 0.99789 | 0.98522 | 0.96832 | 0.94298 | 0.91763
55 | 0.91447 | 0.94298 | 0.97043 | 0.98944 | 1.0011 | 1.0074 | 1.0074 | 1.0042 | 0.99683 | 0.98416 | 0.96621 | 0.93981 | 0.91447
60 | 0.9113 | 0.9377 | 0.96727 | 0.98733 | 1 | 1.0063 | 1.0063 | 1.0042 | 0.99578 | 0.98205 | 0.96199 | 0.93453 | 0.9113
65 | 0.90391 | 0.93136 | 0.96304 | 0.98522 | 1 | 1.0053 | 1.0063 | 1.0032 | 0.99366 | 0.97994 | 0.95776 | 0.92819 | 0.90391
70 | 0.8944 | 0.92397 | 0.95882 | 0.98205 | 0.99789 | 1.0042 | 1.0053 | 1.0011 | 0.99261 | 0.97677 | 0.95248 | 0.9208 | 0.8944
75 | 0.8849 | 0.91552 | 0.95354 | 0.97994 | 0.99472 | 1.0021 | 1.0032 | 0.99894 | 0.9905 | 0.97254 | 0.9472 | 0.91235 | 0.8849
80 | 0.87434 | 0.90602 | 0.94615 | 0.97571 | 0.99261 | 1 | 1 | 0.99578 | 0.98627 | 0.96832 | 0.94087 | 0.9018 | 0.87434
85 | 0.85956 | 0.8944 | 0.93875 | 0.96938 | 0.98944 | 0.99578 | 0.99578 | 0.99261 | 0.98205 | 0.9641 | 0.93242 | 0.89124 | 0.85956
90 | 0.84583 | 0.88173 | 0.93031 | 0.9641 | 0.98416 | 0.99155 | 0.9905 | 0.98733 | 0.97782 | 0.95565 | 0.92397 | 0.87856 | 0.84583